## Slide 1: Distribution of Loss of Load Events in 2017 IRM PBC
Mike Welch
Planning Engineer, Reliability Planning
NYSRC ICS
March 1, 2017
Rensselaer, NY

## Slide 2: Case Description
2017 IRM Preliminary Base Case (PBC)
  1500 Replications
  NYCA LOLE of 0.0998
Summer Peak Load Forecast from 2016 GB
  Zone J: 11,795 MW
  Zone K: 5,422 MW
  G – J Locality: 16,313 MW
  NYCA: 33,363 MW

## Slide 3: IRM 2017 PBC Results
Load Level |  | Base Shape | Weight | NYCA Daily Events | NYCA LOLE (dys/yr)
1 | (Highest) | 2006 | 0.0062 | 4,138 | 0.0171
2 |  | 2002 | 0.0606 | 1,731 | 0.0699
3 |  | 2007 | 0.2417 | 62 | 0.0100
4 |  | 2007 | 0.3830 | 8 | 0.0020
5 |  | 2007 | 0.2417 | 4 | 0.0006
6 |  | 2007 | 0.0606 | 1 | 0.0000
7 | (Lowest) | 2007 | 0.0062 | 0 | 0
Total: |  |  | 1.0000 | 5,944 | 0.0998

## Slide 4: IRM 2017 PBC Results
NYCA LOLE (dys/yr)
Load Level | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | Annual
1 | 0 | 0 | 0 | 0 | 0 | 0.0000 | 0.0020 | 0.0151 | 0 | 0 | 0 | 0 | 0.0171
2 | 0 | 0 | 0 | 0 | 0.0000 | 0.0002 | 0.0181 | 0.0515 | 0 | 0.0000 | 0 | 0 | 0.0699
3 | 0 | 0 | 0 | 0 | 0.0002 | 0.0003 | 0.0015 | 0.0077 | 0.0003 | 0 | 0 | 0 | 0.0100
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0003 | 0.0015 | 0.0003 | 0 | 0 | 0 | 0.0021
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007 | 0 | 0 | 0 | 0 | 0.0007
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0000 | 0 | 0 | 0 | 0 | 0.0000
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: | 0 | 0 | 0 | 0 | 0.0002 | 0.0006 | 0.0218 | 0.0765 | 0.0006 | 0.0000 | 0 | 0 | 0.0998

## Slide 5: IRM 2017 PBC Results
Load Level | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | 
1 | 24,514 | 24,551 | 24,341 | 21,404 | 28,733 | 30,072 | 35,149 | 37,278 | 25,858 | 23,788 | 23,566 | 25,546 | 
2 | 22,467 | 21,963 | 21,475 | 23,415 | 25,130 | 33,442 | 35,641 | 36,223 | 31,165 | 27,627 | 23,236 | 25,252 | 
3 | 23,841 | 24,885 | 24,340 | 20,758 | 26,521 | 33,596 | 34,186 | 34,891 | 31,057 | 27,693 | 22,513 | 24,600 | 
4 | 23,418 | 24,444 | 23,909 | 20,390 | 25,187 | 31,908 | 32,466 | 33,127 | 29,500 | 26,302 | 22,114 | 24,164 | 
5 | 22,879 | 23,881 | 23,358 | 19,920 | 23,775 | 30,121 | 30,646 | 31,262 | 27,853 | 24,830 | 21,604 | 23,607 | 
6 | 22,151 | 23,121 | 22,615 | 19,287 | 22,337 | 28,299 | 28,789 | 29,360 | 26,175 | 23,329 | 20,917 | 22,856 | 
7 | 21,236 | 22,166 | 21,681 | 18,490 | 21,023 | 26,634 | 27,094 | 27,630 | 24,638 | 21,962 | 20,053 | 21,912 | 
NYCA LFU-Adjusted Load (MW)

## Slide 6
8/01
8/02
8/03
7/31
8/04
8/04
8/03
8/02
7/31
8/03
8/01
8/04
7/17
7/18
7/27
8/07
7/26
8/16
7/05
8/15
7/05
8/18
8/17
8/09
7/11
7/10
6/28
6/27
8/08
6/29

## Slide 7
The Mission of the New York Independent System Operator, in collaboration with its stakeholders, is to serve the public interest and provide benefit to consumers by:
  Maintaining and enhancing regional reliability
  Operating open, fair and competitive wholesale electricity markets
  Planning the power system for the future
  Providing factual information to policy makers, stakeholders and investors in the power system
www.nyiso.com

## Slide 8: Supplemental Inforamtion
INTERNAL USE ONLY

## Slide 9: Reliability Metric Definitions
Loss of Load Event (hrs/yr)
  Max Value of 8760 (8784)
Loss of Load Event (dys/yr)
  Max Value of 365 (366)
  Reliability Criteria: 0.100
Loss of Expected Energy (MWh/yr)
  Maximum Determined by Energy in Load Shape
INTERNAL USE ONLY

## Slide 10: IRM 2017 PBC Results
Load Level | Base Shape | Weight | NYCA Events |  | Reliability Metrics |  | 
 |  |  | Hourly | Daily | LOLE | LOLE | LOEE
 |  |  |  |  | (hrs/yr) | (dys/yr) | (MWh/yr)
1 | 2006 | 0.0062 | 18,186 | 4,138 | 0.0752 | 0.0171 | 57.22
2 | 2002 | 0.0606 | 4,824 | 1,731 | 0.1949 | 0.0699 | 105.02
3 | 2007 | 0.2417 | 123 | 62 | 0.0198 | 0.01 | 5.4
4 | 2007 | 0.3830 | 10 | 8 | 0.0026 | 0.002 | 1.28
5 | 2007 | 0.2417 | 4 | 4 | 0.0006 | 0.0006 | 0.23
6 | 2007 | 0.0606 | 1 | 1 | 0 | 0 | 0.01
7 | 2007 | 0.0062 | 0 | 0 | 0 | 0 | 0
Total: |  | 1.0000 | 23,148 | 5,944 | 0.2931 | 0.0998 | 169.17
INTERNAL USE ONLY

## Slide 11: IRM 2017 PBC Results
NYCA LFU Multipliers (Calculated)
Load Level | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | 
1 | 1.04 | 1.04 | 1.04 | 1.04 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.04 | 1.04 | 
2 | 1.03 | 1.03 | 1.03 | 1.03 | 1.08 | 1.09 | 1.09 | 1.09 | 1.09 | 1.08 | 1.03 | 1.03 | 
3 | 1.02 | 1.02 | 1.02 | 1.02 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.02 | 1.02 | 
4 | 1.00 | 1.00 | 1.00 | 1.00 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 1.00 | 1.00 | 
5 | 0.98 | 0.98 | 0.98 | 0.98 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.98 | 0.98 | 
6 | 0.94 | 0.94 | 0.94 | 0.94 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.94 | 0.94 | 
7 | 0.91 | 0.91 | 0.91 | 0.91 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.91 | 0.91 | 
INTERNAL USE ONLY

## Slide 12: IRM 2017 PBC Results
LOLE (hrs/yr)
Load Level | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | Annual
1 | 0 | 0 | 0 | 0 | 0 | 0.0000 | 0.0040 | 0.0711 | 0 | 0 | 0 | 0 | 0.0752
2 | 0 | 0 | 0 | 0 | 0.0000 | 0.0004 | 0.0453 | 0.1492 | 0 | 0.0000 | 0 | 0 | 0.1949
3 | 0 | 0 | 0 | 0 | 0.0002 | 0.0003 | 0.0027 | 0.0163 | 0.0003 | 0 | 0 | 0 | 0.0198
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0003 | 0.0020 | 0.0003 | 0 | 0 | 0 | 0.0026
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007 | 0 | 0 | 0 | 0 | 0.0007
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0000 | 0 | 0 | 0 | 0 | 0.0000
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: | 0 | 0 | 0 | 0 | 0.0002 | 0.0007 | 0.0523 | 0.2393 | 0.0006 | 0.0000 | 0 | 0 | 0.2931
INTERNAL USE ONLY

## Slide 13: IRM 2017 PBC Results
LOEE (MWh/yr)
Load Level | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | Annual
1 | 0 | 0 | 0 | 0 | 0 | 0.00 | 0.62 | 56.60 | 0 | 0 | 0 | 0 | 57.22
2 | 0 | 0 | 0 | 0 | 0.01 | 0.15 | 15.31 | 89.54 | 0 | 0.02 | 0 | 0 | 105.02
3 | 0 | 0 | 0 | 0 | 0.04 | 0.05 | 0.62 | 4.55 | 0.15 | 0 | 0 | 0 | 5.41
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1.18 | 0.09 | 0 | 0 | 0 | 1.28
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 0 | 0 | 0 | 0.23
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0.01
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: | 0 | 0 | 0 | 0 | 0.05 | 0.21 | 16.56 | 152.10 | 0.24 | 0.02 | 0 | 0 | 169.17
INTERNAL USE ONLY

## Slide 14
Peak Load: 33,363 MW
Peak Load: 33,363 MW
Peak Hour, Load Level 1
Peak Hour, Load Level 2
Peak Hour, Load Level 3
INTERNAL USE ONLY

## Slide 15
Peak Load: 33,363 MW
Peak Hour, Load Level 1
(No Events)
(No Events)
Up To 6 hrs
Up To 8 hrs
Up To 9 hrs
Up To 7 hrs
Up To 4 hrs
INTERNAL USE ONLY

## Slide 16
INTERNAL USE ONLY

## Slide 17
Monday
Peak Load: 33,363 MW
Up to 6 hours in duration, Level 2
Loss of Load Hours
INTERNAL USE ONLY

## Slide 18
Tuesday
Peak Load: 33,363 MW
Up to 5 hours in duration, Level 2
Loss of Load Hours
Up to 8 hours in duration, Level 1
INTERNAL USE ONLY

## Slide 19
Wednesday
Peak Load: 33,363 MW
INTERNAL USE ONLY

## Slide 20
Thursday
Peak Load: 33,363 MW
INTERNAL USE ONLY

## Slide 21
Friday
Peak Load: 33,363 MW
INTERNAL USE ONLY