## Slide 1: Analyzing Loss of Load Events
Mike Welch
SENIOR PLANNING ENGINEER, SYSTEM & RESOURCE PLANNING, NYISO
NERC PAF 2019

## Slide 2: Roles of the NYISO
Planning for New York’s energy future
  Assessing needs over a 10-year horizon and evaluating projects proposed to meet those needs
Advancing the technological infrastructure of the electric system
  Developing and deploying information technology and tools to make the grid smarter
Reliable operation of the bulk electricity grid
  Managing the flow of power on 11,000 circuit-miles of transmission lines from hundreds of generating units
Administration of open and competitive wholesale electricity markets
  Bringing together buyers and sellers of energy and related products and services

## Slide 3
NYISO by the numbers

## Slide 4: Reliability Planning at the NYISO
The Reliability Planning Process (RPP) is one of the foundational components of the Comprehensive System Planning Process (CSPP)
The RPP sets a biennial process where we perform:
  The Reliability Needs Assessment (RNA) to understand possible threats to reliability in the next 10 years
  The Comprehensive Reliability Plan (CRP) to evaluate and if necessary select solutions to identified needs from the RNA

## Slide 5: Performing Probabilistic Studies
The NYISO uses GE MARS
  We apply a criterion that at no point in time will the probability of the unplanned disconnection of firm load exceed 0.1 days per year
General study parameters:
  A 10 year study period (e.g. 2021-2030 for the upcoming 2020 RNA)
  We apply 7 load forecast uncertainty levels to the load forecast
We have started looking at new ways to review our case results, as described in this presentation

## Slide 6: Test Case Overview
Assumptions for a hypothetical 2026 power system:
  Use 2026 load forecast from the 2019 “Gold Book” Load and Capacity Data
  Resource mix adjusted from the existing generation fleet
  Transfer limits based on 2019 CRP topology
  No energy storage resources are modeled (e.g. batteries)
We simulate 10,000 Monte Carlo replications
Notes: What was the peak load in 2018? Overall?

## Slide 7: Test Case Results
Metric | Base Case
LOLE (dy/yr) | 0.0881
LOLH (hr/yr) | 0.3188
LOEE (MWh/yr) | 187.19

## Slide 8: Developing Insights
We can superimpose load and event data, plotting:
  the adjusted load values
  the hourly energy deficiencies (LOEE)
This lets us see where the events are occurring

## Slide 9: Developing Insights
We can create a heatmap to show where the events are occurring
For the test case, events are concentrated in:
  the summer months, and
  the highest load levels

## Slide 10
Developing
New Insights

## Slide 11: Event Duration
By processing the margin data for each area, we were able aggregate the hourly events into daily events
The higher load levels show a bias for longer events

## Slide 12: Event Summary
  Summarizes the hourly deficiencies – MinDef/MaxDef
  Total unserved energy – EnergyDef
Replication | Date | Load Level | Duration (hours) | MinDef (MW) | MaxDef (MW) | EnergyDef (MWh)
1 | 2026-08-04 | 1 | 5 | 325.00 | 1,688.57 | 5,547.22
1 | 2026-08-05 | 1 | 8 | 116.69 | 2,032.46 | 10,890.41
1 | 2026-08-06 | 1 | 3 | 893.04 | 1,133.82 | 3,105.14
2 | 2026-08-04 | 1 | 2 | 104.04 | 559.09 | 663.13
2 | 2026-08-05 | 1 | 6 | 360.41 | 1,023.90 | 4361.00

## Slide 13
What’s Next?

## Slide 14: Applying Analysis to Energy Storage
The Event Summary contains the information to model a simple energy storage resource, such as:
  Length of Event
  Maximum Deficit during the Event
  Overall Energy Deficit from the Event
Using MATLAB® we developed a simple battery storage model to reduce deficits

## Slide 15: Simple Battery Storage Model
Assumptions:
  Batteries are fully charged at the start of each event
  Batteries are local resources and cannot assist neighboring areas
Parameters:
  23 Batteries Modeled in New York
  Total 2,000 MW nameplate
  Total 9,000 MWh of storage

## Slide 16: Impact of Battery Storage
Future Work:
  Add a charging constraint
  Define round-trip efficiency constraint
Metric | Base Case | Battery Scenario | Delta
LOLE (dy/yr) | 0.0881 | 0.0208 | -0.0673
LOLH (hr/yr) | 0.3188 | 0.0757 | -0.2431
LOEE (MWh/yr) | 187.19 | 49.53 | -134.66
Avg. Duration (hr) | 2.31 | 1.32 | -0.99

## Slide 17
Questions?

## Slide 18: Our mission, in collaboration with our stakeholders, is to serve the public interest and provide benefit to consumers by:
  Maintaining and enhancing regional reliability
  Operating open, fair and competitive wholesale electricity markets
  Planning the power system for the future
  Providing factual information to policymakers, stakeholders and investors in the power system